## Hartvigsen
V jet = sqrt(2*g*h) |  |  | 20 | spoons | Turbine Efficiency | Generator Efficiency | water to wire
Q = Vjet * Anozzles | m/sec * 100 -> cm/sec |  | 0.49 | blue = 0.49 | 83% | 84% | 69.72%
| cm^3/sec / 1000 -> l/sec |  |  | green = 0.757
User Inputs are in yellow highlighted cells. |  |  |  | orange = 1.0
rho kg/liter | 0.998
g (m/sec^2) | 9.81 |  |  |  | 32 | Nozzle # (bore in 1/64")
Normal Ranges -> | 50% Theoretical |  | 9cm with blue spoons |  |  | 6-13mm with blue spoons
-> | 44%-50% Typical |  | 15-30 cm with red spoons |  | 1 to 4 Nozzles | 10-26mm with red spoons
|  |  | Runner Pitch Diameter |  | # of Nozzles | Nozzle Diameter |  | Nozzle Area (cm^2)
Operating (%Vjet) | 49% |  | 8.5131 | (cm) | 4 | 12.7 | (mm) | 5.0671
Nozzle Velocity Coef. | 0.98 |  | 3.3516 | (in) |  | 0.5 | (in)
Nozzle contraction Coef. | 0.97
Nozzle discharge Coef. | 0.9506
0.1 | delta Head | Peak Power | Peak Power |  |  |  | Results in US Units for Head, Power, and Flow
Head (m) | Vjet (m/s) | Runner V (m/s) | RPM | Flow (liter/sec) | Turbine Power (kW) | Electric Power (kW) | Head (ft) | Turbine (hp) | Flow (gpm) | Flow (CFS) | psi
24 | 21.2658 | 10.4202 | 2337.7214 | 10.4523 | 2.0384 | 1.7123 | 78.7402 | 2.7336 | 165.6897 | 0.36918 | 34.0945
23.9 | 21.2214 | 10.3985 | 2332.8461 | 10.4305 | 2.0257 | 1.7016 | 78.4121 | 2.7165 | 165.3442 | 0.36841 | 33.9524
23.8 | 21.177 | 10.3767 | 2327.9605 | 10.4086 | 2.013 | 1.6909 | 78.084 | 2.6995 | 164.9979 | 0.36764 | 33.8104
23.7 | 21.1324 | 10.3549 | 2323.0647 | 10.3867 | 2.0003 | 1.6803 | 77.7559 | 2.6825 | 164.6509 | 0.36687 | 33.6683
23.6 | 21.0878 | 10.333 | 2318.1586 | 10.3648 | 1.9877 | 1.6697 | 77.4278 | 2.6655 | 164.3032 | 0.36609 | 33.5262
23.5 | 21.0431 | 10.3111 | 2313.242 | 10.3428 | 1.9751 | 1.6591 | 77.0997 | 2.6486 | 163.9547 | 0.36532 | 33.3842
23.4 | 20.9983 | 10.2892 | 2308.315 | 10.3208 | 1.9625 | 1.6485 | 76.7717 | 2.6317 | 163.6055 | 0.36454 | 33.2421
23.3 | 20.9534 | 10.2671 | 2303.3774 | 10.2987 | 1.9499 | 1.6379 | 76.4436 | 2.6149 | 163.2555 | 0.36376 | 33.1001
23.2 | 20.9083 | 10.2451 | 2298.4292 | 10.2766 | 1.9374 | 1.6274 | 76.1155 | 2.5981 | 162.9048 | 0.36298 | 32.958
23.1 | 20.8632 | 10.223 | 2293.4703 | 10.2544 | 1.9249 | 1.6169 | 75.7874 | 2.5813 | 162.5534 | 0.3622 | 32.8159
23 | 20.818 | 10.2008 | 2288.5007 | 10.2322 | 1.9124 | 1.6064 | 75.4593 | 2.5645 | 162.2011 | 0.36141 | 32.6739
22.9 | 20.7727 | 10.1786 | 2283.5203 | 10.2099 | 1.8999 | 1.5959 | 75.1312 | 2.5478 | 161.8481 | 0.36062 | 32.5318
22.8 | 20.7273 | 10.1564 | 2278.529 | 10.1876 | 1.8875 | 1.5855 | 74.8031 | 2.5312 | 161.4944 | 0.35984 | 32.3898
22.7 | 20.6818 | 10.1341 | 2273.5267 | 10.1652 | 1.8751 | 1.5751 | 74.4751 | 2.5145 | 161.1398 | 0.35905 | 32.2477
22.6 | 20.6362 | 10.1117 | 2268.5134 | 10.1428 | 1.8627 | 1.5647 | 74.147 | 2.4979 | 160.7845 | 0.35825 | 32.1056
22.5 | 20.5905 | 10.0893 | 2263.489 | 10.1204 | 1.8504 | 1.5543 | 73.8189 | 2.4814 | 160.4284 | 0.35746 | 31.9636
750